Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to Murdock Manufacturing; Morris Group International ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Murdock Manufacturing; Morris Group International, 15125 Proctor Ave., City of Industry, CA 91746; Phone: (626) 333-2543 | (800) 591-9081; Fax: <Insert Fax number>; Website: www.murdockmfg.com; Email: dyoung@acorneng.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 224713 - DRINKING FOUNTAINS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Drinking fountains.

          - Bottle filling stations.

          - Supports.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of drinking fountain and bottle filling station.

          - Include construction details, material descriptions, dimensions of individual components and profiles, and finishes.

          - Include operating characteristics, and furnished specialties and accessories.

Retain "Sustainable Design Submittals" Paragraph below if required to attain sustainability rating or to track sustainability submittals.

        - Sustainable Design Submittals:

"Product Data" Subparagraph below applies to LEED (including v4), IgCC, ASHRAE 189.1, and Green Globes for fixtures and equipment that consume water.

          - Product Data: For water consumption.

Retain "Product Data" Subparagraph below to require minimum recycled content for LEED 2009, MRc 4, "Recycled Content."

          - Product Data: For recycled content, indicating postconsumer and preconsumer recycled content and cost.

        - Shop Drawings:

          - Include diagrams for power wiring.

      - CLOSEOUT SUBMITTALS

        - Maintenance Data: For [drinking fountains] [and] [bottle filling stations] to include in maintenance manuals.

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Filter Cartridges: Equal to <Insert number> percent of quantity installed for each type and size indicated, but no fewer than <Insert number> of each.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

        - Standards:

The U.S. Safe Drinking Water Act (SDWA) has required national compliance with less than or equal to 0.25 percent weighted average lead content at wetted surfaces for pipe, fittings, and devices intended to convey or dispense water for human consumption since January 2014. The IPC and UPC have the same requirements. Items in compliance with NSF 61 and NSF 372 also comply with this requirement. Some manufacturers choose to meet this requirement through independent testing and have "Certified Lead Free" products, which may or may not have NSF 61 or NSF 372 certifications.

          - Drinking fountains and bottle filling stations intended to convey or dispense water for human consumption are to comply with the U.S. Safe Drinking Water Act (SDWA), requirements of the Authority Having Jurisdiction (AHJ), and with NSF 61 or NSF 372, or be certified in compliance with NSF 61 or NSF 372 by an ANSI-accredited third-party certification body, that the weighted average lead content at wetted surfaces is less than or equal to 0.25 percent.

Retain first subparagraph below if stainless steel drinking fountains or bottle filling stations are retained.

          - [Comply with ASME A112.19.3/CSA B45.4 for stainless steel drinking fountains and bottle filling stations.]

Retain first subparagraph below if vitreous china drinking fountains are retained.

          - [Comply with ASME A112.19.2/CSA B45.1 for vitreous china drinking fountains.]

          - Comply with NSF 42 and NSF 53 for water filters for drinking fountains and bottle filling stations.

          - Comply with ICC A117.1 for accessible drinking fountains and bottle filling stations.

      - DRINKING FOUNTAINS

Copy "Drinking Fountains - Pedestal Concrete" Paragraph below and re-edit for each type of drinking fountain required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Pedestal Concrete <Insert drawing designation>: [wheelchair accessible] [, pet fountain] [, freeze resistant].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed. Note: Coordinate fixture model number with concrete aggregate desired color.

GUF98 Series, pedestal-mounted drinking fountain

GUF99 Series, pedestal-mounted drinking fountain

GUT19-PF Series, pet fountain

GVF19 Series, pedestal-mounted drinking fountain

GVJ19 Series, barrier-free, pedestal-mounted drinking fountain

GVM49 Series, barrier-free, bi-level, pedestal-mounted drinking fountain

GVQ89 Series, barrier-free, tri-level, pedestal-mounted drinking fountain

          - Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [GUF98] [GUF99] [GUT18-PF] [GUT19-PF] [GVF18] [GVF19] [GVJ18] [GVJ19] [GVM48] [GVM49] [GVQ88] [GVQ89] or comparable product by one of the following:

            - Haws Corporation.

            - Petersen Manufacturing Co., Inc.

            - Stern-Williams Co., Inc.

            - <Insert manufacturer's name>.

          - Standards:

            - Comply with:

              - NSF 61 and NSF 372.

              - Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC)

              - ASME A112.18.1/CSA B125.

              - IAPMO IGC 226-2019

Retain first subparagraph below for wheelchair-accessible drinking fountains.

              - ICC A117.1, CSA B651, 2010 ADA Standard for Accessible Design.

          - Pedestal:

Retain "with offset to receptor" in "Type" Subparagraph below for wheelchair-accessible drinking fountains.

            - Type: [Square] [Round] [with side receptor(s)] [with offset to receptor] [, freeze resistant] [, pet option].

            - Material: Reinforced [brown] [tan] concrete aggregate.

          - Receptor(s):

            - Number: [One] [Two] [Three].

            - Material: Type 304 stainless steel polished to a #4 satin finish.

            - Shape: [Square] [Round].

            - Bubbler: One for each receptor, stainless steel, anti-rotation, non-squirt design.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: 0.5 gpm (0.0316 L/s).

          - Controls: Pneumatic push-button and air-actuated valve.

          - Access to Internal Components: Panel in pedestal.

          - Supply: NPS 1/2 (DN 15) with shutoff valve and 100-mesh strainer.

          - Drain Piping: NPS 1-1/4 (DN 32) minimum trap and waste.

Retain "Pet Fountain Receptor" Subparagraph below only when needed to comply with Project design requirements.

          - Pet Fountain Receptor: Housing material and finish to match fixture, push-button control, waterspout, Type 304 stainless steel bowl polished to a #4 satin finish, grid drain.

Retain "Freeze-Resistant Supply Fittings" Subparagraph below for freeze-resistant drinking fountains.

          - Freeze-Resistant Supply Fittings: Below-grade water supply connection with PVC housing cylinder containing removable control valve assembly, shut-off, check valve(s), and tubing for supply riser(s) and pneumatic push button(s).[ Provide non-pollutable piston valve assembly to prevent cross contamination with ground water.]

            - Bury Depth, Grade to Valve Components: 36 inches to 67 inches (915 mm to 1702 mm) adjustable depth.

"Total Number of Stations" Subparagraph below should reflect the total fixture device outlets for drinking fountain(s) bottle filler and pet fountain.

            - Total Number of Stations: [One] [Two] [Three] [Four].

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements. Verify available options with basis-of-design manufacturer's standard selections.

          - Accessories:

In-ground valve access box is only offered with freeze-resistant supply fittings.

            - In-ground, freeze-resistant valve access box with lid.

            - Child height 30-inch bubbler height.

            - Foot spray.

            - Hose bibb, compression, with hose threaded outlet and vacuum breaker.

            - Hose bibb, loose key, with hose threaded outlet and vacuum breaker.

            - Hose bibb, loose key, recessed vandal resistant, with hose threaded outlet and vacuum breaker.

            - In-ground mounting plate.

            - Jug filler, spigot, self-closing valve with plain end.

            - Jug filler, push-button, self-closing valve with plain end.

            - Square concrete step for pedestal fountain.

        - Drinking Fountains - Outdoor, Pedestal, Stainless Steel <Insert drawing designation> [bottle filler] [, wheelchair accessible] [pet fountain] [, freeze resistant].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

GRF35 Series, pedestal-mounted drinking fountain

GRM45 Series, barrier-free, bi-level, pedestal-mounted drinking fountain

GRQ45 Series, pedestal-mounted drinking fountain

GRJ85 Series, barrier-free, pedestal-mounted drinking fountain

GYM74 Series, pedestal-mounted bottle filler with drinking fountain

GYV34 Series, barrier-free outdoor pedestal bi-level drinking fountain with bottle filler

GYQ84 Series, pedestal-mounted bottle filler with bi-level drinking fountain

GYW44 Series, barrier-free outdoor pedestal dual bottle filler with drinking fountain

GRT75-PF Series, outdoor pet fountain

GSF55 Series, pedestal-mounted drinking fountain

GSM55 Series, barrier free, bi-level, pedestal-mounted drinking fountain

GSQ45 Series, barrier-free, tri-level, pedestal-mounted drinking fountain

GSJ95 Series, barrier-free, pedestal-mounted drinking fountain

GWF55 Series, pedestal-mounted drinking fountain

GWQ84 Series, pedestal-mounted hand washing station with bottle filler and drinking fountain

M-PM14 Series, pet fountain with hose bibb

M-PM24 Series, pet shower with pet fountain and leash hook

M-PM34 Series, pet fountain

M-PM74 Series, dual station pet fountain

          - Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [GRF35] [GRM45] [GRQ45] [GRJ85] [GYM74] [GYV34] [GYQ84] [GYW44] [GRT75-PF] [GSF55] [GSM55] [GSQ45] [GSJ95] [GWF55] [GWQ84] [M-PM14] [M-PM24] [M-PM34] [M-PM74] or comparable product by one of the following:

            - Most Dependable Fountains, Inc.

            - Stern-Williams Co., Inc.

            - <Insert manufacturer's name>.

          - Standards:

            - Comply with:

              - NSF 61 and NSF 372.

              - Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC)

              - ASME A112.18.1/CSA B125.

              - IAPMO IGC 226-2019

Retain first subparagraph below for wheelchair-accessible drinking fountains.

              - ICC A117.1, CSA B651, 2010 ADA Standard for Accessible Design.

Retain "with offset to receptor" option in "Pedestal" Subparagraph below for wheelchair-accessible drinking fountains.

          - Pedestal: [Square] [Round], [with offset to receptor] [with side receptor(s)] [, with bottle filler] [, freeze resistant] [, pet fountain].

            - Material: 12-gage Type 304 stainless steel.

            - Finish: [Stainless steel #4 satin finish] [Powder coat with manufacturer's standard colors offered] <Insert color>.

          - Receptor(s):

            - Number: [One] [Two] [Three].

            - Material: 18-gage Type 304 stainless steel polished to a #4 satin finish.

            - Shape: [Square] [Round].

            - Bubbler: One for each receptor, stainless steel, anti-rotation, non-squirt design.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: 0.5 gpm (0.0316 L/s).

          - Control:

Retain one of first two subparagraphs below. Basis-of-design manufacturer provides push button with steam regulator on units with drinking fountain only and pneumatic push buttons on units with bottle filler.

            - Push button with cartridge style valve with front access adjustable stream regulator.

            - Pneumatic push-button and air-actuated valve.

          - Access to Internal Components: Panel in pedestal.

          - Supply Piping: NPS 1/2 (DN 15). Provide with shutoff valve and 100-mesh strainer.

          - Drain Piping: NPS 1-1/4 (DN 32) minimum.

Retain "Bottle Filler" Subparagraph below for outdoor drinking fountain models with bottle filler. "Filtration Subparagraph is not included for models with "Freeze-resistant supply" option.

          - Bottle Filler: Integrated with fixture material and finish.

            - Activation:

Retain one of first two subparagraphs below as required to suit Project requirements. Dual operation is basis-of-design manufacturer's standard.

              - Dual operation: Pneumatic hemispherical push button requiring less than 5 pounds of force with air-actuated valve and 9-volt infrared sensor and battery power pack.

              - Pneumatic hemispherical push button requiring less than 5 pounds of force with air-actuated valve.

            - Spout: Laminar flow spout preset with 20-second automatic shut-off timer.

            - Drain: Type 304 stainless steel screen with waste tube connector.

            - Filtration: Lead, chlorine, and cyst reduction filter rated for 1500-gallon effective lifespan.

Retain "Freeze-Resistant Supply Fitting" Subparagraph below for freeze-resistant drinking fountains.

          - Freeze-Resistant Supply Fittings: Below-grade water supply connection with PVC housing cylinder containing removable air-actuated control valve assembly, shut-off, check valve(s), and tubing for supply riser(s) and pneumatic push button(s).[ Provide non-pollutable piston valve assembly to prevent cross-contamination with ground water.]

            - Bury Depth, Grade to Valve Components: 36 to 67 inches (915 to 1702 mm) adjustable depth.

"Total Number of Stations" Subparagraph below should reflect the total fixture device outlets for drinking fountain(s) bottle filler and pet fountain.

            - Total Number of Stations: [One] [Two] [Three] [Four].

Retain "Pet Fountain Receptor" Subparagraph below only when needed to comply with Project design requirements.

          - Pet Fountain Receptor: Housing material and finish to match fixture, push-button control, waterspout, Type 304 stainless steel bowl polished to a #4 satin finish, grid drain.

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements. Verify available options with basis-of-design manufacturer's standard selections.

          - Accessories:

In-ground valve access box is only offered with freeze-resistant supply fittings.

            - In-ground (freeze-resistant) valve access box with lid.

            - Child height 30-inch" bubbler height.

            - Foot spray.

            - Hose bibb, compression, with hose threaded outlet and vacuum breaker.

            - Hose bibb, loose key, with hose threaded outlet and vacuum breaker.

            - Hose bibb, loose key, recessed vandal resistant, with hose threaded outlet and vacuum breaker.

            - In-ground mounting plate.

            - Jug filler, spigot, self-closing valve with plain end.

            - Jug filler, push-button, self-closing valve with plain end.

Copy "Drinking Fountains" Paragraph below and re-edit for each type of wall-mounted drinking fountain required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Wall-Mounted Concrete <Insert drawing designation> [, wheelchair accessible] [, freeze resistant].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

GVC59 Series, barrier free, wall-mounted drinking fountain. Note: Coordinate fixture model number with concrete aggregate desired color.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [GVC58] [GVC59] or comparable product by one of the following:

            - Elkay Manufacturing Co.

            - Filtrine Manufacturing Company.

            - Halsey Taylor.

            - <Insert manufacturer's name>.

          - Standards:

            - Comply with:

              - NSF 61 and NSF 372.

              - Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC)

              - ASME A112.18.1/CSA B125.

              - IAPMO IGC 226-2019

Retain first subparagraph below for wheelchair-accessible drinking fountains.

              - ICC A117.1, CSA B651, 2010 ADA Standard for Accessible Design.

          - Receptor: Square, 18-gage Type 304 stainless steel polished to a #4 satin finish.

          - Casing Arm: Reinforced [brown] [tan] concrete aggregate.

          - Maximum Water Flow: 0.5 gpm (1.89 L/min).

          - Control: Pneumatic push-button and air-actuated valve.

          - Drain: Grid type with NPS 1-1/4 (DN 32) minimum waste.

          - Supply Piping: NPS 1/2 (DN 15). Provide with shutoff valve and 100-mesh strainer.

          - Waste Piping: NPS 1-1/4 (DN 32).

          - Retain "Freeze-Resistant Supply and Fittings" Subparagraph below for freeze-resistant drinking fountains. Assembly is intended for installation above ground directly behind unit in an enclosed area that remains above freezing.

          - Freeze-Resistant Supply and Fittings: Above-ground, freeze-resistant, galvanized steel box with louvered cover, containing air-actuated control valve(s) assembly, drain down device, p-trap waste fitting, supply riser(s) and tubing for pneumatic push button(s).

            - Total number of stations: One.

          - Drinking Fountain Mounting Height: [Standard] [Disabled accessible in accordance with ICC A117.1] [Child-height for children's use].

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements.

          - Accessories:

            - Concealed support carrier.

Copy "Drinking Fountains" Paragraph below and re-edit for each type of wall-mounted drinking fountain required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Wall mounted, stainless steel <Insert drawing designation> [bi-level] [, bottle filler] [, vandal resistant] [, wheelchair accessible] [, freeze resistant].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Note: The following models are rated for indoor use only.

A171400S-FG-VR, barrier-free, 14-gage stainless steel, enhanced vandal resistance, wall-mounted drinking fountain

A172400S-FG-VR, barrier free, 14-gage stainless steel, enhanced vandal resistance, bi-level, wall-mounted drinking fountain

A171400S-FG-VR-BFS, barrier-free, 14-gage stainless steel, enhanced vandal resistance, wall-mounted drinking fountain with bottle filler

A172400S-FG-VR-BFS, barrier-free, 14-gage stainless steel, enhanced vandal resistance, bi-level, wall-mounted drinking fountain with bottle filler

A171-UG Series, barrier-free, wall-mounted drinking fountain

A172-UG Series, barrier-free, bi-level, universal bi-level, wall-mounted drinking fountain

A171-UG-BF Series, barrier-free, wall-mounted, drinking fountain with push-button or sensor-operated bottle filler

A172-UG-BF Series, barrier-free, wall-mounted universal bi-level drinking fountain push-button or sensor-operated bottle filler

A171-UG-SO Series, sensor-operated, barrier-free, wall-mounted drinking fountain

A172-UG-SO Series, sensor-operated, barrier-free, universal bi-level, wall-mounted drinking fountain

A171-UG-SO-BF Series, sensor-operated, barrier-free, wall-mounted drinking fountain with bottle filler

A172-UG-SC-BF Series, sensor-operated, barrier-free, universal bi-level, wall-mounted drinking fountain with bottle filler

A171-UG-SOC Series, barrier-free, concealed sensor operated, wall-mounted, drinking fountain

A172-UG-SOC Series, barrier free, concealed sensor operated, wall-mounted universal bi-level drinking fountain

A171-UG-SOC-BF Series, barrier-free, concealed sensor operated, wall-mounted, drinking fountain

A172-UG-SOC-BF Series, barrier-free, concealed sensor operated, wall-mounted universal bi-level drinking fountain

A171-UG-VR Series, barrier-free, vandal-resistant button, wall-mounted drinking fountain

A172-UG-VR Series, barrier-free, vandal-resistant button, universal bi-level, wall-mounted drinking fountain

A171-UG-VR-BF Series, barrier-free, vandal-resistant button, wall-mounted drinking fountain with push-button or sensor-operated bottle filler

A172-UG-VR-BF Series, barrier-free, vandal-resistant button, universal bi-level, wall-mounted drinking fountain with push-button or sensor-operated bottle filler

A171-UG-VR-D1-BFS Series, barrier-free, vandal-resistant, wall-mounted drinking fountain with vandal-resistant, push-button or sensor-operated bottle filler

A172-UG-VR-D1-BFS Series, barrier-free, vandal-resistant, universal bi-level, wall-mounted drinking fountain with vandal-resistant, push-button or sensor-operated bottle filler

A191 Series, barrier-free, wall-mounted drinking fountain

A191-BF Series, barrier-free, wall-mounted drinking fountain with bottle filler and trim panel

A192 Series, barrier-free, bi-level, wall-mounted drinking fountain with 42-inch trim panel

A192-BF Series, barrier-free, bi-level, wall-mounted drinking fountain with bottle filler and 42-inch trim panel

A4A1 Series, wall-mounted economy drinking fountain

A4B1 Series, wall-mounted economy drinking fountain

M-DFBF Series, heavy-duty, barrier-free, wall-mounted drinking fountain with concealed sensor and bottle filler with sensor operation

Note: The following models are rated for both Indoor and Outdoor use.

GRC75 Series, barrier-free, wall-mounted drinking fountain

GSC55 Series, barrier-free, wall-mounted drinking fountain

GWA74 Series, wall-mounted drinking fountain

GWB24 Series, wall-mounted drinking fountain

GRE24 Series, barrier-free, bi-level, wall-mounted drinking fountain

GYE14 Series, wall-mounted drinking fountain, push-button-operated bottle filler

GYE24 Series, barrier free, bi-level, wall-mounted drinking fountain, push-button-operated bottle filler

          - Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [A171400S-FG-VR] [A172400S-FG-VR] [A171400S-FG-VR-BFS] [A172400S-FG-VR-BFS] [A171-UG] [A172-UG] [A171-UG-BF] [A172-UG-BF] [A171-UG-SO] [A172-UG-SO] [A171-UG-SO-BF] [A172-UG-SO-BF] [A171-UG-SOC] [A172-UG-SOC] [A171-UG-SOC-BFS] [A172-UG-SOC-BF] [A171-UG-VR] [A172-UG-VR] [A171-UG-VR-BFS] [A172-UG-VR-BF] [A171-UG-VR-D1-BF] [A172-UG-VR-D1-BF] [A191] [A191-BF] [A192] [A192-BF] [A4A1] [A4B1] [M-DFBF] [GRC75] [GSC55] [GWA74] [GWB24] [GRE24] [GYE14] [GYE24] or comparable product by one of the following:

            - Elkay Manufacturing Co.

            - Filtrine Manufacturing Company.

            - <Insert manufacturer's name>.

          - Standards:

            - Comply with:

              - NSF 61 and NSF 372.

              - Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC)

              - ASME A112.18.1/CSA B125.

              - IAPMO IGC 226-2019

Retain first subparagraph below for wheelchair-accessible drinking fountains.

              - ICC A117.1, CSA B651, 2010 ADA Standard for Accessible Design.

          - Receptor:

            - Shape: [Square] [Round].

            - Material: Type 304 stainless steel polished to a #4 satin finish.

          - Bubblers: [One] [Two], [flexible bubbler with gray finish,] [lead-free stainless steel bubbler], anti-rotation, non-squirt design.

          - Maximum Water Flow: 0.5 gpm (0.0316 L/s).

In "Cabinet" Subparagraph below, "Stainless steel with powder coat finish" option is only offered with models GRC75, GRD65-BP6, GSC55, GSD75-BP6, GRE24, GYE14, and GYE24.

          - Cabinet: [Stainless steel with #4 satin finish] [Steel with powder coat finish] [Stainless steel with powder coat finish] <Insert color>.

Retain "Back Panel" Subparagraph below only for models GRE24, GYE14, and GYE24.

          - Back Panel: Stainless steel wall plate 1/4 inch (6 mm) thick with finish to match cabinet.

Retain "Accessible Drinking Fountain Orientation" Subparagraph below for models GRE24, GYE14, and GYE24.

          - Accessible Drinking Fountain Orientation: On [left] [right] side when facing unit.

Retain one of two options in first "Control" Subparagraph below. Basis-of-design manufacturer provides push button with stream regulator on units with drinking fountain only and pneumatic push button on units that include a bottle filler.

          - Control: [Push button with cartridge style valve with front access adjustable stream regulator] [Pneumatic push button with air-actuated valve].

Retain first "Control" Subparagraph below for models A4A1, A4B1, GWA74, and GWB24.

          - Control: Stainless steel lead-free bubbler with push button.

Retain first "Control" Subparagraph below for models A171-UG-SO, A172-UG-SO, A171-UG-SO-BF, and A172-UG-SO-BF with front apron sensor; and models A171-UG-SOC, A172-UG-SOC, A171-UG-SOC-BF, and A172-UG-SOC-BF with undermount sensor.

          - Control: Infrared sensor preset with 20-second maximum run time.

            - Sensor Location: [Front apron] [Undermount concealed].

            - Valve: 9-volt dc electronic solenoid valve.

Retain "Control" Subparagraph below for models GYE14, GYE24, and GRE24. Basis-of-design manufacturer's standard control is push-button cartridge valve.

          - Control: [Push button with cartridge style valve with front access adjustable stream regulator] [Undermount concealed infrared sensor preset with 20-second maximum run time].

Retain "Sensor Location" and "Valve" subparagraphs below for models specified with undermount concealed infrared sensor.

            - Sensor Location: Undermount concealed.

            - Valve: 9-volt dc electronic solenoid valve with battery pack and wire harness.

When bottle filler is required, retain one of three "Bottle Filler" subparagraphs below.

Retain first "Bottle Filler" Subparagraph below when required for models A171400S-FG-VR-BFS, A172400S-FG-VR-BFS, A171-UG-VR-D1-BF, and A172-UG-VR-D1-BF.

          - Bottle Filler: Accessible vandal-resistant design with coordinated installation for single station drinking fountain and bi-level accessible station. Drinking fountain basin will serve as drain.

            - Housing: 18-gage Type 304 stainless steel with exposed surfaces polished to a #4 satin finish.

            - Activation:

Retain one of first two subparagraphs below when required to suit Project requirements.

              - 9-volt infrared sensor, preset with 20-second automatic shut-off timer with [115-volt plug-in transformer] [battery power pack].

              - Pneumatic hemispherical push button requiring less than 5 pounds of force with air-actuated valve.

            - Spout: Laminar flow spout. Fill rate 1.0 gpm (0.6314 L/s).

Retain "Bottle Counter Display" Subparagraph below when required to suit Project requirements.

            - Bottle Counter Display: LED screen will activate during use to display number of uses that equate to 16-ounce bottles, and water filter status.

              - Provide bottle counter that does not reset due to filter replacement or power interruption.

Retain first "Bottle Filler" Subparagraph below for models A171-UG-BF, A172-UG-BF, A171-UG-SO-BF, A172-UG-SO-BF, A171-UG-SOC-BF, A172-UG-SOC-BF, A171-UG-VR-BF, A172-UG-VR-BF, A191-BF, and A192-BF.

          - Bottle Filler: Accessible contour design for coordinated installation with single station drinking fountain and bi-level accessible station. Drinking fountain basin will serve as drain.

            - Housing: Minimum 20-gage Type 304 stainless steel with exposed surfaces polished to a #4 satin finish with contour to align with drinking fountain basin. Bottle filler area of antimicrobial impact-resistant ABS illuminated by LED light during activation.

            - Activation:

Retain one of first two subparagraphs below when required to suit Project requirements.

              - 9-volt infrared sensor, preset with 20-second automatic shut-off timer with [115-volt plug-in transformer] [battery power pack].

              - Pneumatic hemispherical push button requiring less than 5 pounds of force for air-actuated valve.

            - Spout: Laminar flow spout. Fill rate 1.0 gpm (0.6314 L/s).

Retain "Bottle Counter Display" Subparagraph below when required to suit Project requirements.

            - Bottle Counter Display: LED screen will activate during use to display number of uses that equate to 16-ounce bottles, and water filter status.

              - Provide bottle counter that does not reset due to filter replacement or power interruption.

Retain "Bottle Filler" Subparagraph below for models GYE14 and GYE24. "Filtration" Subparagraph is not included for models with "Freeze-resistant supply" option.

          - Bottle Filler: Extra height, integrated with fixture material and finish.

            - Activation:

Retain one of first two subparagraphs below when required to suit Project requirements. Pneumatic push-button control is basis-of-design manufacturer's standard.

              - Pneumatic hemispherical push button requiring less than 5 pounds of force for air-actuated valve.

              - 9-volt infrared sensor, preset with 20-second automatic shut-off timer with [115-volt plug-in transformer] [battery power pack].

            - Spout: Laminar flow spout. Fill rate 1.0 gpm (0.6314 L/s).

            - Drain: Type 304 stainless steel screen with waste tube connector.

            - Filtration: Lead, chlorine, and cyst reduction filter rated for 1500-gallon effective lifespan.

"Freeze-Resistant Supply and Fittings" Subparagraph below is offered on select outdoor drinking fountains. Assembly is intended for installation above ground directly behind unit in an enclosed area that remains above freezing.

Offered on the following basis-of-design manufacturer's units suitable for outdoor installation: Models GRC75, GRD65-BP6, GSC55, GSD75-PB6, GRE24, GYE14, and GYE24. Bi-level units receive two separate boxes containing freeze-resistant supply and fittings.

          - Freeze-Resistant Supply and Fittings: Above-ground, freeze-resistant, galvanized steel box with louvered cover, containing control valve(s) assembly, drain down device, p-trap waste fitting, supply riser(s) and tubing for pneumatic push button(s).

"Total Number of Stations" Subparagraph below should reflect the total fixture device outlets for drinking fountain(s) and bottle filler.

            - Total Number of Stations: [One] [Two] [Three].

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply Piping: NPS 1/2 (DN 15). Provide with shutoff valve and 100-mesh strainer.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) p-trap and waste.

          - Filtration:

Retain one of the two subparagraphs below when required. “EZ Door” is a brand name of Murdock Manufacturing, and is offered as an option for A17 Series units only, with the exception of -SO, -SOC, and -FG models.

            - Lead, chlorine, and cyst reduction filter rated for [1500 gal (6800 L)] [3000 gal (13600 L)]-gallon effective lifespan.

            - Provide [EZ Door] filter assembly with lockable cover, allowing access beneath skirt for replacement with lead, chlorine, and cyst reduction filter rated for 1500 gal (6800 L) effective lifespan. Furnish key for each unit having lockable cover furnished for Project.

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements. Verify available options with basis-of-design manufacturer's standard selections.

          - Accessories:

            - Back panel splash plate.

            - Cane skirt kit for upper unit (bi-level fountains).

            - Concealed support carrier.

Coordinate first subparagraph below with "Filtration" Subparagraph above.

            - Drop-down filter access door.

Copy "Drinking Fountains" Paragraph below and re-edit for each type of wall-mounted drinking fountain required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Wall mounted, white enamel coated cast iron <Insert drawing designation>: [Bi-level] [Trough] [wheelchair accessible].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

A151J Series, barrier-free, white enamel coated cast iron, wall-mounted drinking fountain

A1I2J Series, barrier-free, two-station, white enamel coated cast iron, wall-mounted drinking fountain

A152J Series, barrier-free, white enamel coated cast iron, wall-mounted drinking fountain with back panel

          - Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [A151J] [A1I2J] [A152J] or comparable product by one of the following:

            - Haws Corporation.

            - Halsey Taylor.

            - <Insert manufacturer's name>.

          - Standards:

            - Comply with:

              - NSF 61 and NSF 372.

              - Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC)

              - ASME A112.18.1/CSA B125.

              - IAPMO IGC 226-2019

Retain first subparagraph below for wheelchair-accessible drinking fountains.

              - ICC A117.1, CSA B651, 2010 ADA Standard for Accessible Design.

          - Material: Cast iron with white enamel coating.

In "Bubblers" Subparagraph below, "Push-button bubbler, stainless steel, lead-free" option is only offered on basis-of-design manufacturer's models A151J and A152J. If selected, delete "Control" Subparagraph below.

          - Bubblers: [One] [Two], [lead-free stainless steel bubbler] [push-button bubbler, stainless steel, lead-free], located on deck with anti-rotation, non-squirt design.

          - Control:

            - Push button with cartridge style valve with front access adjustable stream regulator.

          - Maximum Water Flow: 0.5 gpm (0.0316 L/s).

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) chrome-plated brass P-trap and waste.

Retain "Freeze-Resistant Supply and Fittings" Subparagraph below for freeze-resistant drinking fountains. Assembly is intended for installation above ground directly behind unit in an enclosed area that remains above freezing.

          - Freeze-Resistant Supply and Fittings: Above-ground, freeze-resistant, galvanized steel box with louvered cover, containing air-actuated control valve(s) assembly, drain down device, p-trap waste fitting, supply riser(s) and tubing for pneumatic push button(s).

            - Total Number of Stations: [One] [Two].

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements.

          - Accessories:

            - Concealed support carrier.

          - Drinking Fountain Mounting Height: [Standard] [Disabled accessible in accordance with ICC A117.1] [Child-height for children's use].

Copy "Drinking Fountains" Paragraph below and re-edit for each type of wall-mounted, semirecessed drinking fountain required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Stainless Steel wall mounted with trim panel <Insert drawing designation>: [, bi-level] [, bottle filler] [, vandal resistant] [, semi-recessed].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

A131-VR Series, barrier-free, vandal-resistant, wall-mounted drinking fountain

A132-VR Series, barrier-free, vandal-resistant, bi-level, wall-mounted drinking fountain with 32-inch panel

A151-FG Series, barrier-free, 14-gage stainless steel, wall-mounted drinking fountain

A152-FG Series, barrier free, bi-level, wall-mounted, 14-gage stainless steel drinking fountain with 32-inch trim panel

A151-VR Series, barrier-free, vandal-resistant, wall-mounted drinking fountain

A152-VR Series, barrier-free, vandal-resistant, bi-level, wall-mounted drinking fountain with 32-inch trim panel

A131-VR-BF Series, barrier-free, vandal-resistant, wall-mounted drinking fountain with semi-recessed bottle filler

A132-VR-BF Series, barrier-free, vandal-resistant, bi-level, wall-mounted drinking fountain with semi-recessed bottle filler

A151-FG-BF Series, barrier-free, 14 gage stainless steel, wall-mounted drinking fountain with semi-recessed bottle filler

A152-FG-BF Series, barrier-free, bi-level, wall-mounted, 14-gage stainless steel drinking fountain with semi-recessed bottle filler and 32-inch trim panel

A151-VR-BF Series, barrier-free, vandal-resistant, wall-mounted drinking fountain with semi-recessed bottle filler

A152-VR-BF Series, barrier-free, vandal-resistant, bi-level, wall-mounted drinking fountain with semi-recessed bottle filler and 32-inch trim panel

GRD65-BP6 Series, barrier-free, bi-level, wall-mounted drinking fountain

GSD75-BP6, barrier free, bi-level, wall-mounted drinking fountain

M-OBR4-GRC Series, recessed outdoor bottle filler with GRC drinking fountain

M-OBR4-GRD Series, recessed outdoor bottle filler with bi-level drinking fountain

          - Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [A131-VR] [A132-VR] [A151-FG] [A152-FG] [A151-VR] [A152-VR] [A131-VR-BF] [A132-VR-BF] [A151-FG-BF] [A152-FG-BF] [A151-VR-BF] [A152-VR-BF] [GRD65-BP6] [GSD75-BP6] [M-OBR4-GRC] [M-OBR4-GRD] or comparable product by one of the following:

            - Elkay Manufacturing Co.

            - Oasis International.

            - <Insert manufacturer's name>.

          - Standards:

            - Comply with:

              - NSF 61 and NSF 372.

              - Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC)

              - ASME A112.18.1/CSA B125.

              - IAPMO IGC 226-2019

Retain first subparagraph below for wheelchair-accessible drinking fountains.

              - ICC A117.1, CSA B651, 2010 ADA Standard for Accessible Design.

          - Receptor Shape: [Square] [Round].

          - Back Panel: Stainless steel wall plate behind drinking fountain with #4 satin finish.

          - Bubbler: [Flexible bubbler with gray finish] [Stainless steel bubbler], located on deck, anti-rotation, non-squirt design.

          - Maximum Water Flow: 0.5 gpm (0.0316 L/s).

Retain "Accessible Drinking Fountain Orientation" Subparagraph below only for A132 series and A152 series bi-level models.

          - Accessible Drinking Fountain Orientation: On [left] [right] side when facing unit.

          - Control: Push button with cartridge style valve with front access adjustable stream regulator.

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Supply Piping: NPS 1/2 (DN 15). Provide with shutoff valve and 100-mesh strainer.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) P-trap and waste.

Retain "Bottle Filler" subparagraph below as required to suit Project requirements.

          - Bottle Filler: Accessible vandal-resistant design integrated into trim panel for single station drinking fountain and bi-level accessible station.

            - Activation:

Retain one of first four subparagraphs below.

Sensor operation is basis-of-design manufacturer's standard for models A131-VR, A132-VR, A151-FG, A152-FG, A151-VR, A152-VR, A131-VR-BF, A132-VR-BF, A151-FG-BF, A152-FG-BF, A151-VR-BF, and A152-VR-BF.

              - 9-volt infrared sensor, preset with 20-second automatic shut-off timer with 115-volt plug-in transformer.

Models M-OBR4-GRC and M-OBR4-GRD are provided standard with dual-control activation with both sensor and push button and are offered with options for battery-operated sensor or push-button control only.

              - Dual control with direct acting push button and 9-volt infrared sensor, preset with 115-volt plug-in transformer.

              - Dual control with direct acting push button and 9-volt infrared sensor, preset with 20-second automatic shut-off timer with battery-powered operation.

              - Push-button control only.

            - Spout: Laminar flow spout. Fill rate 1.0 gpm (0.6314 L/s).

            - Drain: Type 304 stainless steel screen with waste tube connector.

Retain "Filtration" Subparagraph below when needed to comply with Project design requirements.

            - Filtration: Lead, chlorine, and cyst reduction filter rated for 1500-gallon effective lifespan.

Retain "Bottle Counter Display" Subparagraph below when required to suit Project requirements.

            - Bottle Counter Display: LED screen will activate during use to display number of uses that equate to 16-ounce bottles, and water filter status.

              - Provide bottle counter that does not reset due to filter replacement or power interruption.

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements. Verify available options with basis-of-design manufacturer's standard selections.

          - Accessories:

            - Filter access panel (bi-level units).

            - Back panel splash plate.

            - Cane skirt kit for upper unit (bi-level fountains).

            - Concealed support carrier.

            - High-polish stainless steel.

Retain "Cooling System" Subparagraph below when needed to comply with Project requirements.

          - Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

            - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

            - Comply with ASHRAE 15, or where applicable, ASHRAE 34.

          - Capacities and Characteristics:

            - Capacity: 8 gal (30 l) per hour.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Electrical Characteristics:

              - Motor Horsepower 1/5 HP (149 W).

              - Compressor: [115 Volt, 60 Hertz, 4.6 Amps] [220 Volt, 50 Hertz, 2.5 Amps].

              - Certification: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application. Will conform with NSF/ANSI 61, Section 9 and CHSC 116875.

            - Refrigerant: R134a.

            - Chilled water lines to be insulated.

          - Support:

Retain one of two subparagraphs below. Retain first subparagraph for basis-of-design manufacturer's models GRD65-BP6 and GSD75-BP6.

            - Fixture mounting plate with brackets for attaching to wood blocking or substrate.

Retain subparagraph below for basis-of-design manufacturer's models A131-VR, A132-VR, A151-FG, A152-FG, A151-VR, A152-VR, A131-VR-BF, A132-VR-BF, A151-FG-BF, A152-FG-BF, and A151-VR-BF.

            - In-wall mounting frame to receive fixture trim plate.

Copy "Drinking Fountains" Paragraph below and re-edit for each type of stainless steel, recessed drinking fountain required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Stainless steel, recessed <Insert drawing designation>: [cuspidor] [, wheelchair accessible].

Retain "Basis-of-Design Product" Subparagraph below and list of manufacturers to require products from manufacturers listed or a comparable product from other manufacturers.

A181 Series, barrier-free, fully recessed wall-mounted drinking fountain

A181CUSP Series, barrier free, fully recessed wall-mounted drinking fountain and cuspidor

A180CUSP Series, barrier free, fully recessed wall-mounted cuspidor

A481 Series, fully recessed, wall-mounted drinking fountain

A481CUSP Series, fully recessed, wall-mounted drinking fountain and cuspidor

A480CUSP Series, fully recessed, wall-mounted cuspidor

          - Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [A181] [A181CUSP] [A180CUSP] [A481] [A481CUSP] [A480CUSP] or comparable product by one of the following:

            - Elkay Manufacturing Co.

            - Filtrine Manufacturing Company.

            - <Insert manufacturer's name>.

          - Standards:

              - NSF 61 and NSF 372.

              - Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC)

              - ASME A112.18.1/CSA B125.

              - IAPMO IGC 226-2019

Retain first subparagraph below for wheelchair-accessible drinking fountains.

              - ICC A117.1, CSA B651, 2010 ADA Standard for Accessible Design.

          - Receptor Shape: Concave with flush wall flange.

          - Drinking Fountain Bubbler: [Flexible bubbler with gray finish,] [Stainless steel bubbler,] One, located on deck, anti-rotation, non-squirt design.

          - Maximum Water Flow: 0.5 gpm (0.0316 L/s).

Retain "Cuspidor" Subparagraph below for models A181CUSP, A180CUSP, A481, A481CUSP, and A480CUSP.

          - Cuspidor: Provide receptor with stainless steel wash-down outlet in lieu of drinking bubbler.

          - Drinking Fountain Control: Push button with cartridge style valve with front access adjustable stream regulator.

          - Supply Piping: NPS 1/2 (DN 15). Provide with shutoff valve and 100-mesh strainer.

          - Drain: Grid with NPS 1-1/4 (DN 32) minimum horizontal waste and trap, complying with ASME A112.18.2/CSA B125.2.

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements. Verify available options with basis-of-design manufacturer's standard selections.

          - Accessories:

            - Glass filler.

            - High-polish stainless steel.

          - Support: Mounting frame or brackets for attaching to wood blocking or substrate.

Copy "Bottle Filling Station" Paragraph below and re-edit for each type of bottle filling station required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each bottle filling station.

        - Bottle Filling Station <Insert drawing designation>: [Indoor] [Surface-mounted] [Semi-recessed] [, wheelchair accessible] [, vandal-resistant] [bi-level].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

BF3 Series, semi-recessed, push-button, non-refrigerated bottle filler

BF4 Series, semi-recessed, sensor-operated, non-refrigerated bottle filler

BF15 Series, surface-mounted, push-button operated, non-refrigerated bottle filler

BF16 Series, surface-mounted, sensor-operated, non-refrigerated bottle filler

BFEZ16 Series, compact, wall-mounted, sensor-operated, non-refrigerated bottle filler

BFEZ26 Series, compact, wall-mounted universal bi-level, sensor-operated, non-refrigerated bottle filler

M-OBA4 Wall-mounted, sensor/push-button operated outdoor, non-refrigerated bottle filler

          - Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [BF3] [BF4] [BF15] [BF16] [BFEZ16] [BFEZ26] [M-OBA4] or comparable product by one of the following:

            - Elkay Manufacturing Co.

            - Oasis International

            - <Insert manufacturer’s name>.

          - Standards:

              - NSF 61 and NSF 372.

              - Uniform Plumbing Code, National Plumbing Code of Canada (UPC/CUPC)

              - ASME A112.18.1/CSA B125.

              - IAPMO IGC 226-2019

Retain first subparagraph below for wheelchair-accessible drinking fountains.

              - ICC A117.1, CSA B651, 2010 ADA Standard for Accessible Design.

          - Cabinet: Stainless steel with #4 satin finish.

          - Activation:

            - Retain one of first four subparagraphs below.

Push-button control operation is basis-of-design manufacturer's standard for models BF-3 and BF-15.

            - Push-button control.

Infrared sensor control operation is basis-of-design manufacturer's standard for models BF-4, BF-16, BFEZ16, and BFEZ26. Models BF-4 and BF-16 are offered with option for battery-powered sensor operation.

            - 9-volt infrared sensor, preset with 20-second automatic shut-off timer with 115-volt plug-in transformer.

Models BF-4 and BF-16 are offered with option for battery-powered sensor operation.

            - 9-volt infrared sensor, preset with 20-second automatic shut-off timer with battery-powered operation.

Dual control activation with both infrared sensor and push button is basis-of-design manufacturer's standard for Model M-OBA4 and offered with options for battery-operated sensor or push-button control only.

            - Dual control with direct acting push-button and 9-volt infrared sensor, preset with 20-second automatic shut-off timer with battery-powered operation.

            - Dual control with direct acting push-button and 9-volt infrared sensor, preset with 115-volt plug-in transformer.

          - Water Flow Rate: 1.0 GPM, laminar flow spout.

          - Drain: Grid type with NPS 1-1/4 (DN 32).

          - Supply: NPS 3/8 (DN 10) with shutoff valve and 100-mesh strainer.

In "Filtration" Subparagraph below, the 3000-gallon selection is not offered with basis-of-design manufacturer models BF-3 and BF-4.

          - Filtration: Lead, chlorine, and cyst reduction filter rated for [1500] [3000]-gallon effective lifespan.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) p-trap and waste.

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements. Verify available options with basis-of-design manufacturer's standard selections.

          - Accessories:

            - Battery-powered sensor control.

            - Concealed support carrier.

          - Support: [Mounting frame or brackets for attaching to wood blocking or substrate] [or] [in wall mounting frame with fixture mounting plate].

      - BOTTLE FILLING STATIONS

Copy "Bottle Filling Station" Paragraph below and re-edit for each type of bottle filling station required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each bottle filling station.

        - Bottle Filling Station <Insert drawing designation>: [Indoor] [Surface-mounted] [Semi-recessed] [, wheelchair accessible] [, vandal-resistant] [bi-level].

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

BF3 Series, semi-recessed, push-button, non-refrigerated bottle filler

BF4 Series, semi-recessed, sensor-operated, non-refrigerated bottle filler

BF15 Series, surface-mounted, push-button operated, non-refrigerated bottle filler

BF16 Series, surface-mounted, sensor-operated, non-refrigerated bottle filler

BFEZ16 Series, compact, wall-mounted, sensor-operated, non-refrigerated bottle filler

BFEZ26 Series, compact, wall-mounted, universal bi-level, sensor-operated, non-refrigerated bottle filler

M-OBA4 Wall mounted, sensor/push-button operated outdoor, non-refrigerated bottle filler

          - Basis-of-Design Product: Subject to compliance with requirements, provide Murdock Manufacturing; Morris Group International; [BF3] [BF4] [BF15] [BF16] [BFEZ16] [BFEZ26] [M-OBA4] or comparable product by one of the following:

            - Elkay Manufacturing Co.

            - Oasis International.

            - <Insert manufacturer's name>.

          - Standards:

            - Comply with ASME A112.19.3/CSA B45.4.

            - Comply with NSF 61 and NSF 372.

Retain first subparagraph below for wheelchair-accessible drinking fountains.

            - Comply with ICC A117.1.

          - Cabinet: Stainless steel with #4 satin finish.

          - Activation:

Retain one of first four subparagraphs below.

Push-button control operation is basis-of-design manufacturer's standard for models BF-3 and BF-15.

            - Push-button control.

Infrared sensor control operation is basis-of-design manufacturer's standard for models BF-4, BF-16, BFEZ16, and BFEZ26. Models BF-4 and BF-16 are offered with option for battery-powered sensor operation.

            - 9-volt infrared sensor, preset with 20-second automatic shut-off timer with 115-volt plug-in transformer.

Models BF-4 and BF-16 are offered with option for battery-powered sensor operation.

            - 9-volt infrared sensor, preset with 20-second automatic shut-off timer with battery-powered operation.

Dual control activation with both infrared sensor and push button is basis-of-design manufacturer's standard for Model M-OBA4 and offered with options for battery-operated sensor or push-button control only.

            - Dual control with direct acting push button and 9-volt infrared sensor, preset with 20-second automatic shut-off timer with battery-powered operation.

            - Dual control with direct acting push button and 9-volt infrared sensor, preset with 115-volt plug-in transformer.

          - Water Flow Rate: 1.0 GPM, laminar flow spout.

          - Drain: Grid type with NPS 1-1/4 (DN 32).

          - Supply: NPS 3/8 (DN 10) with shutoff valve and 100-mesh strainer.

In "Filtration" Subparagraph below, 3000-gallon selection is not offered with basis-of-design manufacturer's models BF-3 and BF-4.

          - Filtration: Lead, chlorine, and cyst reduction filter rated for [1500] [3000]-gallon effective lifespan.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) p-trap and waste.

All accessories listed in first subparagraph below are optional. Retain only subparagraphs needed to comply with Project design requirements. Verify available options with basis-of-design manufacturer's standard selections.

          - Accessories:

            - Battery-powered sensor control.

            - Concealed support carrier.

          - Support: [Mounting frame or brackets for attaching to wood blocking or substrate] [or] [in wall mounting frame with fixture mounting plate].

      - SUPPORTS

        - Drinking Fountain Carrier:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Josam Company.

            - <Insert manufacturer's name>.

          - Standard: ASME A112.6.1M.

- EXECUTION

      - EXAMINATION

        - Examine roughing-in for water-supply and sanitary drainage and vent piping systems to verify actual locations of piping connections before fixture installation.

        - Examine walls and floors for suitable conditions where fixtures will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install fixtures level and plumb in accordance with roughing-in drawings. For fixtures indicated for children, install at height required by authorities having jurisdiction.

        - Set pedestal drinking fountains and bottle filling stations on flat surface in accordance with manufacturer's written installation instructions.

        - Install recessed, drinking fountains and bottle filling stations secured to wood blocking in wall construction.

        - Install off-the-floor carrier supports, affixed to building substrate, for wall-mounted fixtures.

        - Install water-supply piping with shutoff valve on supply to each fixture to be connected to domestic-water distribution piping. Use ball[ or gate] valve. Install valves in locations where they can be easily reached for operation. Valves are specified in Section 220523.12 "Ball Valves for Plumbing Piping"[ and Section 220523.15 "Gate Valves for Plumbing Piping."]

        - Install trap and waste piping on drain outlet of each fixture to be connected to sanitary drainage system.

        - Install wall flanges or escutcheons at piping wall penetrations in exposed, finished locations. Use deep-pattern escutcheons where required to conceal protruding fittings. Comply with escutcheon requirements specified in Section 220518 "Escutcheons for Plumbing Piping."

        - Seal joints between fixtures and walls using sanitary-type, one-part, mildew-resistant, silicone sealant. Match sealant color to fixture color. Comply with sealant requirements specified in Section 079200 "Joint Sealants."

      - PIPING CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Connect fixtures with water supplies, stops, and risers, and with traps, soil, waste, and vent piping. Use size fittings required to match fixtures.

        - Comply with water piping requirements specified in Section 221116 "Domestic Water Piping."

        - Install ball[ or gate] shutoff valve on water supply to each fixture.[ Install valve upstream from filter for drinking fountain.] Comply with valve requirements specified in Section 220523.12 "Ball Valves for Plumbing Piping"[ and Section 220523.15 "Gate Valves for Plumbing Piping."]

        - Comply with soil and waste piping requirements specified in Section 221316 "Sanitary Waste and Vent Piping."

      - ELECTRICAL CONNECTIONS

Retain this article if sensor/hands-free drinking fountains or bottle filling stations are required. Article is not required if sensor/hands-free feature is battery powered.

        - Ground equipment in accordance with Section 260526 "Grounding and Bonding for Electrical Systems."

        - Install electrical devices furnished by manufacturer, but not factory mounted, in accordance with NFPA 70 and NECA 1.

        - Install nameplate for each electrical connection, indicating electrical equipment designation and circuit number feeding connection.

Retain one of two subparagraphs below. First subparagraph cross-references Section 260553 "Identification for Electrical Systems" and should be retained for consistent electrical identification. Second subparagraph is an abbreviated version of the product specified in Section 260553 "Identification for Electrical Systems."

          - Nameplates to be laminated acrylic or melamine plastic signs, as specified in Section 260553 "Identification for Electrical Systems."

          - Nameplates to be laminated acrylic or melamine plastic signs with a black background and engraved white letters at least 1/2 inch (13 mm) high.

      - ADJUSTING

        - Adjust fixture flow regulators for proper flow and stream height.

      - CLEANING

        - After installing fixtures, inspect unit. Remove paint splatters and other spots, dirt, and debris. Repair damaged finish to match original finish.

        - Clean fixtures, on completion of installation, in accordance with manufacturer's written instructions.

        - Provide protective covering for installed fixtures.

        - Do not allow use of fixtures for temporary facilities unless approved in writing by Owner.

END OF SECTION 224713